## Slide 1: Transformer Digital Twin
A physics-informed monitoring and predictive-maintenance prototype for distribution transformer fleets
POWERNEXT AI HACKATHON
Telemetry to dashboard (schematic)
10 synthetic demo assets

## Slide 2: Fixed-interval maintenance misses changing conditions
Periodic inspection
Fixed intervals can miss shifting load and thermal conditions.
Continuous data-informed monitoring
Telemetry-driven view of electrical and thermal condition, with abnormal operation and maintenance guidance surfaced.
Objectives
1
Simulate transformer behaviour
2
Monitor electrical and thermal signals
3
Assess condition
4
Identify abnormal operation
5
Surface maintenance guidance
6
Interactive visualization

## Slide 3: One software twin, one fleet dashboard
Fleet simulator
and historical CSV replay
Canonical schema
data adapter
Backend ingestion
and validation
Empirical ML
analytics
Physics estimator
kept separate
PostgreSQL
persistence
REST API
versioned reads
React / TypeScript
dashboard
The dashboard surfaces alerts, asset state, trends and maintenance context.
1
Shared schema
One canonical schema from source to dashboard
2
Bounded APIs
Bounded snapshots and trends
3
Explicit data provenance
Event identity and source are explicit
4
Per-asset state
State and checkpoints per transformer
5
Deterministic scenarios
Repeatable synthetic demonstrations

## Slide 4: What we ingest and normalize
1
Thermal / environment
Oil temperature
Ambient temperature
2
Electrical
Phase currents L1 / L2 / L3
Phase voltages in canonical telemetry; source VL12 / VL23 / VL31 excluded by the adapter
Active, reactive, apparent power
Power factor
Neutral current
3
Condition / protection
Oil level / oil-leak indicator
Alarms / trips
Loading and asset configuration
!
Oil leak is never inferred from oil temperature alone
An oil-level anomaly appears only when an oil-level sensor or scenario signal exists.
Adapter normalizes to a canonical schema
Checks units, identity and timestamps. Missing values stay null, never zero.

## Slide 5: From simulator to dashboard: one traceable pipeline
Historical CSV
synthetic generator
Canonical adapter
and scenario engine
Modbus register map
(FC04)
Modbus bridge
+ durable spool
MQTT broker
QoS 1
HTTP telemetry
batch / historical replay
Shared FastAPI ingestion
HTTP, batch/replay and MQTT converge here
Schema, units, identity,
timestamp, idempotency checks
Empirical ML pipeline
Opt-in physics demo
PostgreSQL
raw telemetry, receipts, history
committed receipt ack
Versioned REST
read APIs
React + TypeScript
dashboard
Reliability: the bridge removes a spooled item only after checking the backend commit receipt. MQTT acknowledgement alone is not proof of a database commit.

## Slide 6: Architecture: separated responsibilities
Python simulator
Historical CSV replay
Future sensor / SCADA adapter
FastAPI backend
Telemetry and batch APIs
MQTT consumer
Canonical validation + idempotent ingestion
Empirical analytics
Anomaly, health, maintenance
Controlled synthetic physics demo
with 2-D sheet FEM reference
PostgreSQL
Read APIs
latest, history, trends, alerts, maintenance, physics
React / TS operations console
React 19 + TypeScript + Vite
FastAPI + Pydantic + SQLAlchemy
NumPy / pandas / SciPy / scikit-learn
pymodbus + Paho MQTT
Mosquitto + Docker Compose
Stack
Empirical ML and physics estimates are distinct. The physics demo is a physics-informed analytical branch, not an ML model; the production physics contract may return typed "unavailable" results unless eligibility and configuration are satisfied.

## Slide 7: Backend processing protects data integrity
1
Receive event
2
Validate canonical schema
3
Validate asset, time, source and units
4
Deduplicate / idempotency check
5
Per-asset serialization and transaction boundary
6
Persist raw telemetry and receipt
7
Call configured ML / eligible demo adapter
8
Persist versioned results and alert lifecycle
9
Read endpoints serve bounded snapshots and trends
Integrity guarantees
Nullable inputs stay missing; event identity and provenance are explicit
Per-asset state and checkpoints prevent leakage across transformers
A failed physics calculation withholds stale derived values
Versioned APIs separate event time from evaluation / update time

## Slide 8: Analytics turn telemetry into explainable signals
Loading percentage
Apparent-power utilization
Thermal model
Model temperature and residual
Anomaly detection
Anomaly score and flag
Health Index 0–100
Higher is healthier; component scores and reason codes
Maintenance priority
NORMAL / WATCH / PLAN / URGENT with explanatory recommendation
Protection indicators
Oil-level deviation and alarm / trip indicators where inputs exist
Injected abnormal telemetry
Changed loading / thermal / electrical indicators
Health / anomaly reason codes
Alert / maintenance context

## Slide 9: A two-node thermal model drives the digital twin
Tw
winding
To
oil
Ta
ambient
Rw
Ro
Pw
Po
Cw
Co
Governing equations
Co·dTo/dt = Po + (Tw − To)/Rw − (To − Ta)/Ro
Cw·dTw/dt = Pw − (Tw − To)/Rw
To: simplified oil / top-oil-node estimate; Tw: winding node / hot-spot proxy
Controlled synthetic simulation only; not measured top-oil or maximum hot-spot
Units: T[°C] = T[K] − 273.15; ΔT[K] = ΔT[°C]
Exact exponential time advancement of the linear system

## Slide 10: Physics indicators 1–6: thermal and loss formulas
Simulated oil-sensor temp
[°C]
Ts(t+Δt) = To(t) + [Ts(t) − To(t)]·e^(−Δt/τs)
Standalone τs = 5 s; full-stack uses a separate 1200 s lag, passed in as input.
Top-oil temperature estimate
[°C]
T_oil,est = To − 273.15
Oil-node / top-oil proxy from the simplified node model.
Oil-node temperature rise
[K]
ΔTo = To − Ta
Oil-node rise above the held ambient temperature.
Winding hotspot estimate
[°C]
T_winding,proxy = Tw − 273.15
Winding-node proxy, not the true local maximum hot spot.
Winding-to-oil gradient
[K]
ΔT_w−o = Tw − To
Gradient between the winding-node proxy and the oil node.
Total transformer loss
[W]
P_loss = P0 + P_load,rated · (1/3) Σ (Ii / I_rated)²

## Slide 11: Physics indicators 7–10: aging and FEM formulas
Aging acceleration factor
[unitless]
F_age = exp((Tw − 310 K) / 20 K)
The 310 K reference and 20 K scale are invented for the demo; not an IEEE/IEC ageing equation or insulation-life truth.
Equivalent aging hours
[h]
H_eq,new = H_eq,old + (F_prev + F_curr)/2 · Δt/3600
Trapezoidal integration over contiguous synthetic history, Δt in seconds. H = 0 means no supported history; not Remaining Useful Life.
FEM reference temperature
[°C or K]
T_FEM,mean = (1/A) ∫_A Tw(x,y) dA
Area-average winding-sheet temperature of the 2-D two-sheet synthetic FEM; not the maximum point, not a measurement.
Estimator-vs-FEM difference
[K]
ΔT_est−FEM = T_winding,proxy − T_FEM,mean
Matched mean / proxy under the same forcing; near zero tests mean/energy consistency, not spatial hot-spot accuracy.

## Slide 12: Demonstration: controlled fault scenarios
1
Healthy baseline
Reference behaviour
2
Overload
Loading rises; thermal indicators follow
3
Thermal stress
Rapid oil-temperature rise
4
Current imbalance
Phase currents diverge; neutral current rises
5
Low oil level or alarm / trip
Optional, when the field is present
Scenario injection
Coherent telemetry change
Ingestion
Analytics and eligible synthetic physics
Status, trend, alerts, reason codes
Maintenance priority and recommendation

## Slide 13: Roadmap: from synthetic prototype to field evidence
1
Complete manual run-through of the isolated ten-asset stack and browser dashboard
2
Connect real sensors / SCADA via a verified adapter with units, calibration, provenance, timestamps
3
Collect equipment-specific nameplate and loss / thermal parameters from authoritative records
4
Validate thermal behaviour and anomaly alerts on approved field / historical data
5
Release forecasting / RUL only after target definition, testing and external validation
6
Add reporting, maintenance workflow integration, audit trail and utility-system integration
One operational view.
Traceable telemetry.
Explainable thermal calculations.
A clear path from synthetic prototype to evidence-backed transformer monitoring.